PLATEAU ELECTRIC COOPERATIVE

POLICY NO. B4

SUBJECT:
LOCAL WIRING REQUIREMENTS

POLICY:

Plateau Electric requires the following in addition to all other National Electric Code requirements:

A.  All risers shall be installed a minimum of 12 feet from the ground.

B. All risers passing through and above roofs shall be installed a minimum of 36 inches above roof in 2‑inch rigid metal conduit. 

C. The meter base shall be installed a minimum of 5 feet 6 inches above ground and not over 6 feet. 

D. No services shall be attached to trees.

E. No new 2 wire services will be allowed.

F. If multiple conduits are to be attached to a pole, stand-off brackets will be required.
G. If conduits are to be attached to Plateau Electric poles with 600 volts or greater, then the consumer / electrician may request assistance which must be scheduled through the Plateau Electric office where the work shall be performed.  The consumer / electrician shall be required to be present at the job location.
H. No meters shall be installed on primary poles.

I. In the event a primary pole with primary metering attached is changed out, PEC will be responsible for resetting the metering application.  

Adopted:  09-23-24







Effective:  10-01-24
Superseding Policies Adopted:

03-15-11; 9-19-05; 02-09-04; 12-08-03; 10-16-89

